## Power Factor Correction
Power Factor Correction Calculation
Follow the Steps Below to Calculate the Power Factor Correction required for your installation.
Click-On Cells with Blue Text to Modify Values, Results will be Displayed in Green
Step 1. Calculate Actual Load (kW)
(Load) Power kW = Volts V x √3 x Current I x Power factor Pf
|  |  |  | 400 | Nominal Voltage (V)
|  | Non-Corrected Load (kVA) | 692.8 | 1000 | Non-Corrected Current (Amps)
|  | Actual Load (kW) | 415.68 | 0.6 | Non-Corrected Power Factor (CosΦ)
Figures for Current (Amps) and Power Factor (CosØ) can be either Measured or Calculated
Step 2. Calculate Required Power Factor Correction (kVAr)
Power Factor Correction kVAr = Power kW (TanΦi - TanΦd)
Φi = Cosˉ¹ Initial Power Factor Pf
Φd = Cosˉ¹ required Power Factor Pf
|  |  |  | 415.68 | Actual Load (kW)
|  | Correction Required (kVAr) | 417.6126 | 0.6 | Non-Corrected Power Factor (CosΦ)
|  |  |  | 0.95 | Required Power Factor (CosΦ)
Step 3. Calculate Actual Power Factor Correction (kAVr)
Actual Power Factor Correction Pf = Cos (Tanˉ¹ (TanΦi - | [5 empty] | Correction kVAr |  | )
Power kW
|  |  |  | 400 | Correction Applied (kVAr)
|  | Corrected Power Factor (CosΦ) | 0.93754 | 415.68 | Original Load (kW)
|  |  |  | 0.6 | Non-Corrected Power Factor (CosΦ)
Typical Power Factor Correction available in multiples of 25kVAR's, for further details
please Contact Blakley Electrics Technical Department.
Energy Savings for Above Power Factor Correction
| Initial Current | 1000 | Amps |  | Original Load | 692.8 | kVA
| Corrected Current | 639.9729 | Amps |  | Corrected Load | 443.3733 | kVA
| Reduction in Current | 360.0271 | Amps |  | Reduction in Load | 249.4267 | kVA
[5 empty] | Annual CO2 Savings* | 62800 | kg CO2
*C02 Savings based on 500 hours per month.
Click to View Product Data Sheet
Blakley calculator (version 2.0) Blakley Electrics Ltd.