## Sheet1
LOAD LISTING, CALCULATIONS & GENERATOR SIZING
Sr. | Equipment Name | Equip ID No | Absorbed Power | Rated Power | Load Factor | Eff | cosØ | MCC | Nature of Load* | Continous |  | Intermittent |  | Standby |  | Remarks
[10 empty] | KW | KVAR | KW | KVAR | KW | KVAR
1 | Pump Water | WP 1 | 11 | 15 | 0.7 | 0.85 | 0.75 | Maiin | C | 12.9412 | 11.413 | [6 empty] | List |  | (kW) | (kW) | Load Factor | Efficiency | Pwr factor
2 | Pump Water | WP2 | 11 | 15 | 0.7 | 0.85 | 0.75 | Main | C | 12.9412 | 11.413 | [6 empty] | C | 0kW - 15 kW | 0 | 15 | 0.7 | 0.85 | 0.75
3 | Pump Water | WP3 | 11 | 15 | 0.7 | 0.85 | 0.75 | Main | S |  |  |  |  | 12.9412 | 11.413 |  |  | I | 15kW - 45 kW | 15 | 45 | 0.75 | 0.89 | 0.8
4 | Exhaust Fan | FN1 | 3 | 4 | 0.7 | 0.85 | 0.75 | Main | I |  |  | 3.5294 | 3.1126 |  |  |  |  | S | 45kW - 150 kW | 45 | 150 | 0.83 | 0.91 | 0.82
5 | Exhaust Fan | FN2 | 3 | 4 | 0.7 | 0.85 | 0.75 | Main | S |  |  |  |  | 3.5294 | 3.1126 |  |  |  | 150+KW | 150 | + | 0.85 | 0.94 | 0.91
6 | Fire Water Pump | FP1 | 18 | 22 | 0.75 | 0.89 | 0.8 | Emer | I |  |  | 20.2247 | 15.1685
7 | Fire Water Pump | FP2 | 18 | 22 | 0.75 | 0.89 | 0.8 | Emer | S |  |  |  |  | 20.2247 | 15.1685 |  |  | 380
8 | Lighting Load |  | 15 | 20 | 0.75 | 0.89 | 0.8 | Emer | C | 16.8539 | 12.6404 | [6 empty] | 400
415
| Sum | [8 empty] | 42.7363 | 35.4665 | 23.7541 | 18.2812 | 36.6953 | 29.6942
| Maximum Load = | 100% | of continous load + |  | 50% | of Intermittent load + |  |  | 10% | of standby or biggest individual load (higher one)
[10 empty] | KW | KVAR | KVA | cosØ | Amp | Volts
| Maximum of normal running load | [8 empty] | 54.6134 | 44.6071 | 70.5153 | 0.77449 | 101.7801 | 400
| Peak load | [8 empty] | 74.8381 | 59.7757 | 95.7803 | 0.78135 | 138.247 | 400
| Maximum of normal running load with 10% Growth Factor | [8 empty] | 60.0747 | 49.0678 | 77.5669 | 0.77449 | 111.9582 | 400
| Peak load with 10% Growth Factor | [8 empty] | 82.3219 | 65.7532 | 105.3583 | 0.78135 | 152.0717 | 400
| Reccemended Generator Size when | 70% | loading | [6 empty] | 117.6027 | 93.9332 | 150.5119 | 0.78135 | 217.2452 | 400
V - Vital |  | NE - Non essential | b) Absorbed loads: |  |  |  |  | c) Consumed loads: | [5 empty] | 15
E - Essential |  | RS - Restarting | - for pumps, shaft load on duty point; |  |  |  |  | E - "Continuous", all loads that may continuously
a) Load classification/restarting: |  |  | - for instrumentation, computers, commu- |  |  |  |  | be required for normal operation, including
As above |  |  | nication, air conditioning, the required |  |  |  |  | lighting and workshop.
|  |  | load during full operation of plant |  |  |  |  | F - "Intermittent and spares", the loads required
|  |  | - for lighting during dark hours; |  |  |  |  | for intermediate pumping, storage, loading,
|  |  | - for workshops, the average total load in |  |  |  |  | and all electrical spares of electricity
NOTE: |  |  | normal full operation. |  |  |  |  | driven units.
1. Please refer to Single Line Diagrams, DWG-00-E-0001 & DWG-00-E-0002.
2. The loads shown are preliminary and indicative only. Loads shall be updated and finalized after Vendor information.
3. Gas Generator auxiliary loads shall not be considered for the gas generator sizing as the generator output shall be inclusive of these auxiliary loads.
4. In case of failure of one gas generator, when two generators are running, Non-Essential Loads shall be disconnected through Load Shedding System.
5. Essential Loads are the loads which are required when only one gas generator is running and Non-Essential Loads shall be cut off.
When information is not available, the following assumptions are used for LT motors ; |  |  |  | (kW) | (kW) | Load Factor | Efficiency | Pwr factor
| 1 | Motors between: 0kW - 15 kW |  | 0 | 15 | 0.7 | 0.85 | 0.75
| 2 | Motors between: 15kW - 45 kW |  | 15 | 45 | 0.75 | 0.89 | 0.8
| 3 | Motors between: 45kW - 150 kW |  | 45 | 150 | 0.83 | 0.91 | 0.82
| 4 | Motors larger then 150 kW |  | 150 | + | 0.85 | 0.94 | 0.91
3